## Date
This capacity map spreadsheet was updated on | 2024-01-16 09:00
For the latest capacity data please see: https://www.nienetworks.co.uk/connections/capacity-map

## Primary+Dual-Primary
Primary Substation Name | Latitude | Longitude | Voltage Domain | Bulk Supply Point | Transformer Demand Headroom | Upstream Demand Headroom (Distribution Network) | Upstream Demand Headroom (Bulk Supply Point) | Demand Comment | Substation Generation Capacity | Connected Generation | Committed (Not Yet Connected) | Substation Generation Headroom | Upstream Generation Headroom (Distribution Network) | Upstream Generation Headroom (Bulk Supply Point) | Generation Comment | Substation Fault Level Headroom | Upstream Fault Level Headroom (Distribution Network) | Upstream Fault Level Headroom (Bulk Supply Point) | Fault Level Comment | Statement of Works | 33/11kV Transformers Reverse Power Capable? | New 33/11kV Tapchanger Required? | New 33/11kV Relay Required?
Adria | 54.8173 | -7.467 | 33/11kV | STRABANE MAIN | 3.724 | 3.724 | 0 |  | 1.1924 | 1.7734 | 0 | 0 | 10.7866 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 190.4762 | 205.2057 | 571.4286 |  | NIE Networks have planned works to be carried out at this site to make the 33/11kV transformers reverse power capable during RP6 | No | Yes | Yes
Aghagallon | 54.5127 | -6.2878 | 33/11kV | LISBURN MAIN | 0 | 6.9211 | 26.3019 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 0.83746 | 0 | 3.9125 | 10.5574 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 271.9371 | 486.1509 |  |  | Yes | No | No
Ahoghill Central | 54.8497 | -6.3458 | 33/11kV | BALLYMENA RURAL | 7.0831 | 0.5082 | 60.7121 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 11.875 | 1.3561 | 0 | 10.5189 | 11.5799 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 571.4286 | 571.4286 |  |  | Yes | No | No
Airport Road | 54.6039 | -5.8982 | 33/6.6kV | CREGAGH MAIN | 8.9187 | 12.1182 | 4.9036 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 11.4 | 0.162 | 0 | 11.238 | 22.608 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The transformers at this substation are reverse power capable. | 114.2857 | 0 | 0 |  |  | Yes | No | No
Annsborough Central | 54.267 | -5.9262 | 33/11kV | BALLYNAHINCH MAIN | 0 | 0 | 11.7745 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 1.34 | 0 | 3.41 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 468.8286 | 560.7223 |  |  | Yes | No | No
Ardboe Central | 54.6148 | -6.5386 | 33/11kV | DUNGANNON MAIN | 0 | 0 | 0 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 2.0374 | 0.25 | 2.4626 | 17.7366 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 344.9074 | 344.9074 |  |  | Yes | No | No
Ardstraw Central | 54.7301 | -7.4522 | 33/11kV | STRABANE MAIN | 0 | 3.5036 | 0 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 5.7943 | 0.025 | 0 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 205.2057 | 571.4286 |  |  | Yes | No | No
Armagh Central | 54.3296 | -6.6533 | 33/11kV | DRUMNAKELLY MAIN | 1.2288 | 29.4942 | 0 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 0.95367 | 3.5958 | 0.0836 | 0 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 190.4762 | 293.2286 | 370.4823 |  |  | No | Yes | Yes
Armagh North | 54.3602 | -6.6528 | 33/11kV | DRUMNAKELLY MAIN | 2.2793 | 29.4942 | 0 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 0.82879 | 0.31804 | 0.834 | 0 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 190.4762 | 293.2286 | 370.4823 |  |  | No | No | Yes
Ballinamallard West | 54.4314 | -7.627 | 33/11kV | ENNISKILLEN MAIN | 5.3539 | 0 | 28.5689 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 3.6278 | 0 | 1.1222 | 8.1315 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 205.8194 | 423.872 |  |  | Yes | No | No
Ballycastle Central | 55.1971 | -6.2789 | 33/11kV | COLERAINE MAIN | 0 | 0 | 18.827 |  | 11.875 | 3.7525 | 0.165 | 7.9575 | 9.7335 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 320.9086 | 408.576 |  |  | Yes | No | No
Ballyclare Central | 54.7616 | -6.0104 | 33/11kV | LARNE MAIN | 4.9328 | 8.5099 | 0 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 11.4 | 5.8228 | 0.0195 | 5.5577 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 166.7444 | 571.4286 | 571.4286 |  |  | Yes | No | No
Ballyfodrin Central | 54.4382 | -6.4947 | 33/11kV | DRUMNAKELLY MAIN | 0.72393 | 0.72393 | 0 |  | 5.9375 | 1.9723 | 0.5 | 3.4653 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 293.2286 | 370.4823 |  |  | Yes | No | No
Ballygawley South | 54.4596 | -7.0405 | 33/11kV | DUNGANNON MAIN | 2.3107 | 0 | 0 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 1.7285 | 0.225 | 2.7965 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 344.9074 | 344.9074 |  |  | Yes | No | No
Ballygowan Central | 54.5049 | -5.7828 | 33/11kV | ROSEBANK MAIN | 3.844 | 25.0379 | 58.7959 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 9.5 | 1.7432 | 0 | 7.7568 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 0 | 0 |  |  | Yes | No | No
Ballyhenry | 54.6935 | -5.9638 | 33/11kV | CARNMONEY MAIN | 18.1599 | 18.1599 | 23.9527 |  | 0.14874 | 0 | 0 | 0.14874 | 24 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 190.4762 | 148.9166 | 148.9166 |  |  | No | No | Yes
Ballykelly Central | 55.0414 | -7.0219 | 33/11kV | LIMAVADY MAIN | 0.86243 | 17.3394 | 20.5435 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 0.85109 | 0.5 | 3.3989 | 14.2414 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 4.88 | 4.88 |  |  | Yes | No | No
Ballykinler Central | 54.2512 | -5.7984 | 33/11kV | BALLYNAHINCH MAIN | 3.1522 | 0 | 11.7745 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 0.62947 | 0 | 4.1205 | 0.07687 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 468.8286 | 560.7223 |  |  | Yes | No | No
Ballymacarrett | 54.5966 | -5.8871 | 33/6.6kV | KNOCK MAIN | 7.6648 | 7.6648 | 16.9963 |  | 0.79357 | 0.20522 | 0.04 | 0.54835 | 15.0648 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 114.2857 | 571.4286 | 571.4286 |  | NIE Networks have planned works to be carried out at this site to make the 33/11kV transformers reverse power capable during RP6 | No | No | Yes
Ballymacash | 54.5242 | -6.0725 | 33/11kV | LISBURN MAIN | 0.83892 | 1.357 | 26.3019 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 0.41216 | 0.3082 | 0.05 | 0.053963 | 18.5413 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 190.4762 | 271.9371 | 486.1509 |  |  | No | No | Yes
Ballymena East | 54.8727 | -6.261 | 33/11kV | BALLYMENA TOWN | 5.5753 | 23.9963 | 27.0009 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 7.125 | 7.1456 | 0 | 0 | 18.8076 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 29.389 | 0 | 506.3543 |  |  | Yes | No | No
Ballymena North | 54.8742 | -6.2849 | 33/11kV | BALLYMENA TOWN | 0.99644 | 4.7071 | 27.0009 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 0.24572 | 0.075 | 4.4293 | 12.8803 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 0 | 506.3543 |  |  | Yes | No | No
Ballymoney West | 55.0637 | -6.5388 | 33/11kV | COLERAINE MAIN | 5.3213 | 5.3213 | 18.827 |  | 11.4 | 4.2627 | 0 | 7.1373 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 320.9086 | 408.576 |  |  | Yes | No | No
Ballynahinch North | 54.406 | -5.9012 | 33/11kV | BALLYNAHINCH MAIN | 1.4271 | 1.4271 | 11.7745 |  | 7.125 | 3.6867 | 0 | 3.4383 | 20.6808 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 132.4808 | 468.8286 | 560.7223 |  |  | Yes | No | No
Ballysillan | 54.6203 | -5.9632 | 33/6.6kV | BELFAST NORTH MAIN | 5.1585 | 73.7462 | 29.8706 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 11.875 | 0.26616 | 0 | 11.6088 | 13.2538 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The transformers at this substation are reverse power capable. | 29.6133 | 428.6011 | 571.4286 |  |  | Yes | No | No
Balmoral | 54.5654 | -5.9786 | 33/6.6kV | DONEGALL MAIN (SOUTH) | 21.4858 | 21.4858 | 23.3305 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 17.8125 | 0.6829 | 0 | 17.1296 | 19.5122 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The transformers at this substation are reverse power capable. | 114.2857 | 571.4286 | 571.4286 |  |  | Yes | No | No
Banbridge North | 54.3522 | -6.2792 | 33/11kV | BANBRIDGE MAIN | 1.7455 | 23.8328 | 31.2058 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 0.92833 | 0.4608 | 0.451 | 0.01653 | 3.9931 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 164.173 | 398.6571 | 491.7143 |  | NIE Networks have planned works to be carried out at this site to make the 33/11kV transformers reverse power capable during RP6 | No | No | Yes
Bangor Central | 54.6619 | -5.6647 | 33/11kV | RATHGAEL MAIN | 12.8577 | 34.7535 | 28.0689 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 0.95252 | 0.41559 | 0 | 0.53693 | 18.3824 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 60.6994 | 345.2549 | 345.2549 |  | NIE Networks have planned works to be carried out at this site to make the 33/11kV transformers reverse power capable during RP6 | No | Yes | Yes
Bangor East | 54.6553 | -5.6351 | 33/11kV | RATHGAEL MAIN | 10.4166 | 10.4166 | 28.0689 |  | 0.95815 | 1.1275 | 0 | 0 | 17.4725 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 156.6118 | 345.2549 | 345.2549 |  | NIE Networks have planned works to be carried out at this site to make the 33/11kV transformers reverse power capable during RP6 | No | Yes | Yes
Bangor West | 54.6567 | -5.6891 | 33/11kV | RATHGAEL MAIN | 5.924 | 34.7535 | 28.0689 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 0.77156 | 0.51583 | 0 | 0.25573 | 21.3712 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 59.6678 | 345.2549 | 345.2549 |  | NIE Networks have planned works to be carried out at this site to make the 33/11kV transformers reverse power capable during RP6 | No | Yes | Yes
Belleek South | 54.4769 | -8.0868 | 33/11kV | ENNISKILLEN MAIN | 0 | 6.0793 | 28.5689 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 1.3411 | 0 | 3.4089 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 205.8194 | 423.872 |  |  | Yes | No | No
Benburb Central | 54.4037 | -6.7823 | 33/11kV | DRUMNAKELLY MAIN | 0.84142 | 29.4942 | 0 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 2.4192 | 0 | 2.3308 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 293.2286 | 370.4823 |  |  | Yes | No | No
Bentra Central | 54.7572 | -5.736 | 33/11kV | EDEN MAIN | 4.1499 | 4.1499 | 0 |  | 7.125 | 2.7101 | 2 | 2.4149 | 9.6268 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 0 | 0 |  |  | Yes | No | No
Bessbrook North | 54.206 | -6.367 | 33/11kV | NEWRY MAIN | 0.75321 | 11.0635 | 6.2341 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 0.09172 | 0 | 4.6583 | 0.72 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 378.3829 | 567.9451 |  |  | Yes | No | No
Bessbrook South | 54.1853 | -6.3928 | 33/11kV | NEWRY MAIN | 0.62762 | 11.0635 | 6.2341 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 5.9375 | 0.82204 | 0.02 | 5.0955 | 22.5663 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 378.3829 | 567.9451 |  |  | Yes | No | No
Bishopscourt Central | 54.3028 | -5.6096 | 33/11kV | BALLYNAHINCH MAIN | 0.75766 | 0 | 11.7745 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 1.3024 | 0 | 3.4476 | 0.07687 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 468.8286 | 560.7223 |  |  | Yes | No | No
Bog Meadows | 54.5747 | -5.9664 | 33/11kV | DONEGALL MAIN (SOUTH) | 9.0217 | 9.0217 | 23.3305 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 1.363 | 0.33488 | 0.3 | 0.72814 | 19.5122 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 190.4762 | 571.4286 | 571.4286 |  |  | No | No | Yes
Braniel | 54.5763 | -5.8685 | 33/6.6kV | ROSEBANK MAIN | 5.6819 | 5.6819 | 58.7959 |  | 17.8125 | 0.18466 | 0 | 17.6278 | 23.6753 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The transformers at this substation are reverse power capable. | 114.2857 | 0 | 0 |  |  | Yes | No | No
Brookhill Central | 54.5308 | -6.1569 | 33/11kV | LISBURN MAIN | 0 | 6.9211 | 26.3019 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 2.3266 | 0.05 | 2.3734 | 10.5574 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 271.9371 | 486.1509 |  |  | Yes | No | No
Buckna Central | 54.9044 | -6.0905 | 33/11kV | LARNE MAIN | 0.42982 | 0 | 0 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 2.85 | 1.5616 | 0.05 | 1.2384 | 12.6548 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 571.4286 | 571.4286 |  |  | Yes | No | No
Bushmills West | 55.2013 | -6.5303 | 33/11kV | LOGUESTOWN MAIN | 9.3785 | 9.3785 | 9.4204 |  | 11.875 | 2.5439 | 0 | 9.3311 | 14.1601 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 190.4762 | 571.4286 | 571.4286 |  |  | Yes | No | No
Campsie Central | 55.0362 | -7.2019 | 33/11kV | COOLKEERAGH MAIN | 5.5903 | 5.5903 | 57.5972 |  | 7.125 | 2.0734 | 0.005 | 5.0466 | 12.8604 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 50.1371 | 571.4286 | 571.4286 |  |  | Yes | No | No
Cargos Hill | 54.6546 | -5.7253 | 33/11kV | RATHGAEL MAIN | 2.9751 | 0 | 28.0689 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 0.1648 | 0 | 4.5852 | 3.2074 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 345.2549 | 345.2549 |  |  | Yes | No | No
Carn Central | 54.4501 | -6.4098 | 33/11kV | DRUMNAKELLY MAIN | 0 | 23.5725 | 0 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 11.875 | 2.1339 | 0.5 | 9.2411 | 31.0138 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 156.9935 | 293.2286 | 370.4823 |  |  | Yes | No | No
Carnlough Central | 54.9797 | -5.9953 | 33/11kV | LARNE MAIN | 1.9139 | 0 | 0 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 1.1046 | 0 | 3.6454 | 12.6548 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 571.4286 | 571.4286 |  |  | Yes | No | No
Carrickfergus North | 54.7363 | -5.8079 | 33/11kV | EDEN MAIN | 6.4253 | 6.4253 | 0 |  | 17.8125 | 1.9873 | 0 | 15.8252 | 22.4351 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 0 | 0 |  |  | Yes | No | No
Carrickfergus West | 54.7128 | -5.8454 | 33/11kV | EDEN MAIN | 1.5662 | 1.5662 | 0 |  | 1.9753 | 1.7404 | 0.157 | 0.077954 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 190.4762 | 0 | 0 |  | NIE Networks have planned works to be carried out at this site to make the 33/11kV transformers reverse power capable during RP6 | No | Yes | Yes
Carrickblacker Central | 54.4099 | -6.4161 | 33/11kV | DRUMNAKELLY MAIN | 3.121 | 19.3815 | 0 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 1.2648 | 0 | 3.4852 | 15.4432 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 293.2286 | 370.4823 |  |  | Yes | No | No
Carrickmore North | 54.6116 | -7.0509 | 33/11kV | OMAGH MAIN | 0 | 0 | 36.2426 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 3.8 | 4.4504 | 0.025 | 0 | 8.8838 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 170.5097 | 170.5097 |  |  | Yes | No | No
Carrowdore Central | 54.5712 | -5.5622 | 33/11kV | NEWTOWNARDS MAIN | 10.5533 | 15.4122 | 16.2015 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 11.875 | 2.0643 | 0.5 | 9.3107 | 19.7077 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 463.1257 | 571.4286 |  |  | Yes | No | No
Carrs Glen | 54.6286 | -5.9686 | 33/6.6kV | BELFAST NORTH MAIN | 9.1536 | 73.7462 | 29.8706 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 11.4 | 0.91683 | 0 | 0 | 22.2232 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The transformers at this substation are reverse power capable. | 106.0937 | 428.6011 | 571.4286 |  |  | Yes | No | No
Carryduff Central | 54.5147 | -5.8832 | 33/11kV | ROSEBANK MAIN | 12.6253 | 9.7377 | 58.7959 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 11.4 | 2.7855 | 4 | 4.6145 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 115.6907 | 0 | 0 |  |  | Yes | No | No
Castlederg South | 54.7051 | -7.5913 | 33/11kV | STRABANE MAIN | 0 | 3.5036 | 0 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 4.3773 | 0 | 0.37272 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 205.2057 | 571.4286 |  |  | Yes | No | No
Caw | 55.0047 | -7.2718 | 33/11kV | COOLKEERAGH MAIN | 7.923 | 7.923 | 57.5972 |  | 0.47839 | 0.16956 | 0 | 0.30883 | 12.7104 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 190.4762 | 571.4286 | 571.4286 |  |  | No | No | Yes
City Hospital | 54.5874 | -5.9387 | 33/11kV | DONEGALL MAIN (NORTH) | 12.545 | 12.545 | 15.4556 |  | 23.75 | 0.092 | 0 | 23.658 | 26.028 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 571.4286 | 571.4286 |  |  | Yes | No | No
Claudy Central | 54.917 | -7.1847 | 33/11kV | STRABANE MAIN | 1.0434 | 0 | 0 |  | 4.75 | 1.7065 | 0 | 3.0435 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 205.2057 | 571.4286 |  |  | Yes | No | No
Cloghy Central | 54.4252 | -5.5067 | 33/11kV | NEWTOWNARDS MAIN | 1.3452 | 3.4393 | 16.2015 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 0.4318 | 1.044 | 0.0275 | 0 | 19.7077 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 190.4762 | 463.1257 | 571.4286 |  |  | No | Yes | Yes
Cloughmills Central | 55.0027 | -6.3395 | 33/11kV | BALLYMENA RURAL | 5.6879 | 0 | 60.7121 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 11.875 | 4.8928 | 0 | 6.9822 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 571.4286 | 571.4286 |  |  | Yes | No | No
Coagh West | 54.6614 | -6.6869 | 33/11kV | CREAGH MAIN | 5.39 | 5.39 | 8.5217 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 11.875 | 5.5695 | 0.558 | 5.7475 | 3.6148 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 382.2171 | 571.4286 |  |  | Yes | No | No
Coleraine Town | 55.1336 | -6.6582 | 33/11kV | LOGUESTOWN MAIN | 3.5288 | 3.5288 | 9.4204 |  | 2.4904 | 0.98472 | 1.5345 | 0 | 21.7058 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 179.7189 | 571.4286 | 571.4286 |  |  | No | Yes | Yes
Coleraine West | 55.1342 | -6.6952 | 33/11kV | COLERAINE MAIN | 1.153 | 1.153 | 18.827 |  | 1.2518 | 3.5398 | 0.073 | 0 | 9.242 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 190.4762 | 320.9086 | 408.576 |  |  | No | Yes | Yes
Comber Central | 54.5482 | -5.7502 | 33/11kV | ROSEBANK MAIN | 7.0627 | 25.0379 | 58.7959 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 0.65933 | 0.53597 | 0 | 0.12336 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 101.7714 | 0 | 0 |  |  | No | Yes | Yes
Cookstown South | 54.6235 | -6.7328 | 33/11kV | DUNGANNON MAIN | 5.257 | 0 | 0 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 11.4 | 3.0421 | 0.59 | 7.768 | 17.7366 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 344.9074 | 344.9074 |  |  | Yes | No | No
Cookstown West | 54.6249 | -6.7543 | 33/11kV | DUNGANNON MAIN | 0 | 4.4356 | 0 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 2.384 | 0.13 | 2.236 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 344.9074 | 344.9074 |  |  | Yes | No | No
Creagh Central | 54.7689 | -6.5186 | 33/11kV | CREAGH MAIN | 0 | 0 | 8.5217 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 5.9375 | 2.8144 | 0.15 | 2.9731 | 29.7211 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 382.2171 | 571.4286 |  |  | Yes | No | No
Crossgar East | 54.392 | -5.7476 | 33/11kV | BALLYNAHINCH MAIN | 1.2208 | 0.77548 | 11.7745 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 3.8 | 0.80352 | 0 | 2.9965 | 1.7944 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 468.8286 | 560.7223 |  |  | Yes | No | No
Crosshill Central | 54.63 | -6.2052 | 33/11kV | LISBURN MAIN | 6.7718 | 6.9211 | 26.3019 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 11.875 | 2.6785 | 0 | 9.1965 | 10.5574 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 271.9371 | 486.1509 |  |  | Yes | No | No
Crouck Central | 54.7045 | -6.9961 | 33/11kV | OMAGH MAIN | 0 | 19.2401 | 36.2426 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 3.8 | 1.6993 | 0.475 | 1.6257 | 8.8838 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 170.5097 | 170.5097 |  |  | Yes | No | No
Cullybackey Central | 54.8917 | -6.3393 | 33/11kV | BALLYMENA RURAL | 2.2892 | 0 | 60.7121 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 5.9375 | 1.4134 | 0.4 | 4.1241 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 571.4286 | 571.4286 |  |  | Yes | No | No
Cushendall Central | 55.0709 | -6.0576 | 33/11kV | LARNE MAIN | 0 | 0 | 0 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 2.28 | 0.88396 | 0 | 1.396 | 12.6548 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 571.4286 | 571.4286 |  |  | Yes | No | No
Dargan Road | 54.6312 | -5.9105 | 33/6.6kV | BELFAST NORTH MAIN | 18.5818 | 73.7462 | 29.8706 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 0.27638 | 5.821 | 6.42 | 0 | 7.339 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 190.4762 | 428.6011 | 571.4286 |  |  | No | No | Yes
Derryleckagh Central | 54.1772 | -6.285 | 33/11kV | NEWRY MAIN | 0 | 3.2998 | 6.2341 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 1.5275 | 0 | 3.2225 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 378.3829 | 567.9451 |  |  | Yes | No | No
Derrylin Central | 54.1827 | -7.5601 | 33/11kV | AGHYOULE MAIN | 1.1594 | 1.1594 | 6.9382 |  | 4.75 | 2.909 | 0 | 1.841 | 26.381 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 347.0789 | 347.0789 |  |  | Yes | No | No
Donaghadee West | 54.6496 | -5.564 | 33/11kV | RATHGAEL MAIN | 8.3595 | 8.3595 | 28.0689 |  | 11.4 | 1.134 | 0 | 10.266 | 11.836 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 345.2549 | 345.2549 |  |  | Yes | No | No
Downpatrick East | 54.3226 | -5.6873 | 33/11kV | BALLYNAHINCH MAIN | 10.5792 | 0 | 11.7745 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 0.96831 | 2.0231 | 0.297 | 0 | 0.07687 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 190.4762 | 468.8286 | 560.7223 |  |  | No | Yes | Yes
Downpatrick North | 54.3426 | -5.7395 | 33/11kV | BALLYNAHINCH MAIN | 2.7052 | 0 | 11.7745 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 0.67309 | 0.6656 | 0.14 | 0 | 0.07687 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 190.4762 | 468.8286 | 560.7223 |  |  | No | No | Yes
Draperstown North | 54.795 | -6.7725 | 33/11kV | CREAGH MAIN | 1.5488 | 9.0061 | 8.5217 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 2.0366 | 0 | 2.7134 | 29.7211 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 382.2171 | 571.4286 |  |  | Yes | No | No
Dromara | 54.3809 | -6.0069 | 33/11kV | BALLYNAHINCH MAIN | 1.7536 | 0 | 11.7745 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 5.9375 | 3.9017 | 0.2 | 1.8358 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 185.968 | 468.8286 | 560.7223 |  |  | Yes | No | No
Dromore North | 54.5212 | -7.4341 | 33/11kV | ENNISKILLEN MAIN | 6.23 | 6.23 | 28.5689 |  | 11.875 | 4.4779 | 0 | 7.3971 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 205.8194 | 423.872 |  |  | Yes | No | No
Dromore South | 54.4019 | -6.1483 | 33/11kV | BANBRIDGE MAIN | 6.9427 | 16.4961 | 31.2058 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 11.875 | 2.8586 | 4.56 | 4.4564 | 7.0412 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 398.6571 | 491.7143 |  |  | Yes | No | No
Drumahoe West | 54.9773 | -7.2926 | 33/11kV | LISAGHMORE MAIN | 3.2979 | 11.3674 | 4.1257 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 7.125 | 3.6568 | 0 | 3.4682 | 9.1349 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 342.9029 | 448.3589 |  |  | Yes | No | No
Drumcairne Central | 54.5725 | -6.6605 | 33/11kV | DUNGANNON MAIN | 6.128 | 0 | 0 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 11.875 | 1.8415 | 0 | 10.0335 | 17.7366 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 344.9074 | 344.9074 |  |  | Yes | No | No
Dundonald | 54.5938 | -5.8117 | 33/6.6kV | KNOCK MAIN | 4.273 | 4.273 | 16.9963 |  | 17.8125 | 0.25444 | 0 | 17.5581 | 16.3296 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The transformers at this substation are reverse power capable. | 114.2857 | 571.4286 | 571.4286 |  |  | Yes | No | No
Dundonald East | 54.5962 | -5.7863 | 33/11kV | NEWTOWNARDS MAIN | 8.8907 | 7.4532 | 16.2015 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 11.875 | 1.5618 | 0 | 10.3132 | 6.8265 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 463.1257 | 571.4286 |  |  | Yes | No | No
Dungannon North | 54.5092 | -6.7668 | 33/11kV | DUNGANNON MAIN | 1.2232 | 1.2232 | 0 |  | 0.9721 | 0.41487 | 0.025 | 0.53223 | 18.3996 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers required to make the site reverse power capable. | 190.4762 | 344.9074 | 344.9074 |  |  | No | Yes | No
Dungiven Central | 54.9394 | -6.9095 | 33/11kV | LIMAVADY MAIN | 4.108 | 4.108 | 20.5435 |  | 11.875 | 3.1641 | 0 | 8.7109 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 4.88 | 4.88 |  |  | Yes | No | No
Dunmurry South | 54.5449 | -6.0214 | 33/11kV | FINAGHY MAIN | 7.9122 | 7.9122 | 13.7038 |  | 2.3 | 1.1113 | 0.54 | 0.64872 | 12.6899 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. New tapchangers required to make the site reverse power capable. | 81.277 | 118.7086 | 118.7086 |  | NIE Networks have planned works to be carried out at this site to make the 33/11kV transformers reverse power capable during RP6 | No | Yes | No
Dunmurry West | 54.5583 | -6.0173 | 33/11kV | FINAGHY MAIN | 10.0056 | 10.0056 | 13.7038 |  | 1.5377 | 0.74581 | 0.172 | 0.61986 | 17.9352 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 185.085 | 118.7086 | 118.7086 |  |  | No | Yes | Yes
East Lough Road | 54.4844 | -6.3425 | 33/11kV | WARINGSTOWN MAIN | 0 | 0 | 14.4216 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 0.57192 | 0.5 | 3.6781 | 2.5661 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 130.9112 | 443.6731 | 443.6731 |  |  | Yes | No | No
Ederny South | 54.5164 | -7.6684 | 33/11kV | ENNISKILLEN MAIN | 3.1297 | 0 | 28.5689 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 5.9375 | 1.1399 | 0 | 4.7976 | 8.1315 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 205.8194 | 423.872 |  |  | Yes | No | No
Enniskillen East | 54.3567 | -7.6016 | 33/11kV | ENNISKILLEN MAIN | 1.2408 | 14.9396 | 28.5689 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 1.5109 | 0 | 3.2391 | 23.3805 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 205.8194 | 423.872 |  |  | Yes | No | No
Enniskillen Town | 54.3479 | -7.631 | 33/11kV | ENNISKILLEN MAIN | 10.8819 | 14.9396 | 28.5689 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 17.8125 | 0.4334 | 0 | 17.3791 | 23.3805 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 205.8194 | 423.872 |  |  | Yes | No | No
Enniskillen West | 54.3494 | -7.663 | 33/11kV | ENNISKILLEN MAIN | 2.8153 | 6.0793 | 28.5689 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 11.875 | 2.7738 | 0 | 9.1012 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 205.8194 | 423.872 |  |  | Yes | No | No
Falls | 54.5834 | -5.9857 | 33/6.6kV | DONEGALL MAIN (NORTH) | 11.2026 | 11.2026 | 15.4556 |  | 17.8125 | 1.0802 | 0 | 16.7323 | 22.5498 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The transformers at this substation are reverse power capable. | 114.2857 | 571.4286 | 571.4286 |  |  | Yes | No | No
Fivemiletown Central | 54.379 | -7.3159 | 33/11kV | OMAGH MAIN | 5.75 | 5.75 | 36.2426 |  | 5.9375 | 3.3202 | 0 | 2.6173 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 170.5097 | 170.5097 |  |  | Yes | No | No
Fortwilliam | 54.6266 | -5.9403 | 33/6.6kV | BELFAST NORTH MAIN | 6.0319 | 73.7462 | 29.8706 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 1.0768 | 0.38821 | 0 | 0.68856 | 12.9418 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 114.2857 | 428.6011 | 571.4286 |  |  | No | No | Yes
Foyle Road | 54.9916 | -7.3194 | 33/11kV | LISAGHMORE MAIN | 10.5206 | 10.5206 | 4.1257 |  | 1.7007 | 0.7823 | 0.056 | 0.86236 | 22.7141 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 168.2187 | 342.9029 | 448.3589 |  |  | No | Yes | Yes
Garvagh North | 55.0006 | -6.6533 | 33/11kV | COLERAINE MAIN | 3.8631 | 24.3831 | 18.827 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 3.3519 | 0 | 1.3981 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 320.9086 | 408.576 |  |  | Yes | No | No
Glenavy West | 54.5885 | -6.2448 | 33/11kV | LISBURN MAIN | 0 | 6.9211 | 26.3019 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 1.353 | 0 | 3.397 | 10.5574 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 169.0438 | 271.9371 | 486.1509 |  |  | Yes | No | No
Granville Central | 54.4914 | -6.8065 | 33/11kV | DUNGANNON MAIN | 11.176 | 12.9138 | 0 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 17.8125 | 5.6126 | 0 | 12.1999 | 8.3303 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 344.9074 | 344.9074 |  |  | Yes | No | No
Halfpenny Valley | 54.4597 | -6.3593 | 33/11kV | WARINGSTOWN MAIN | 3.8 | 23.5725 | 14.4216 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 1.2251 | 0.15329 | 0.27 | 0.80179 | 31.0138 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 190.4762 | 443.6731 | 443.6731 |  |  | No | No | Yes
Harryville | 54.862 | -6.2773 | 33/11kV | BALLYMENA TOWN | 10.9967 | 10.9967 | 27.0009 |  | 1.3613 | 0.21782 | 0.16 | 0.98352 | 26.3522 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. New tapchangers required to make the site reverse power capable. | 126.9234 | 0 | 506.3543 |  |  | No | Yes | No
Holywood East | 54.6454 | -5.8158 | 33/11kV | RATHGAEL MAIN | 12 | 0 | 28.0689 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 0.86563 | 0.7438 | 0 | 0.12183 | 3.2074 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 190.4762 | 345.2549 | 345.2549 |  |  | No | Yes | Yes
Holywood West | 54.6322 | -5.8458 | 33/11kV | KNOCK MAIN | 8.6534 | 18.1919 | 16.9963 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 0.77874 | 1.4751 | 0 | 0 | 13.3278 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 190.4762 | 571.4286 | 571.4286 |  |  | No | No | Yes
Inver | 54.8461 | -5.8293 | 33/11kV | LARNE MAIN | 13.3699 | 13.3699 | 0 |  | 11.4 | 3.821 | 0 | 7.579 | 10.4276 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 571.4286 | 571.4286 |  |  | Yes | No | No
Keady Central | 54.2461 | -6.7101 | 33/11kV | DRUMNAKELLY MAIN | 0 | 0 | 0 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 0.58171 | 1.2871 | 0.225 | 0 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 190.4762 | 293.2286 | 370.4823 |  |  | No | No | Yes
Kells Central | 54.8114 | -6.2147 | 33/11kV | LARNE MAIN | 0.84316 | 8.5099 | 0 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 5.9375 | 1.1607 | 0 | 4.7767 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 571.4286 | 571.4286 |  |  | Yes | No | No
Kilkeel Central | 54.0713 | -6.0397 | 33/11kV | NEWRY MAIN | 10.2038 | 3.2998 | 6.2341 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 1.75 | 4.5409 | 0.46 | 0 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 190.4762 | 378.3829 | 567.9451 |  | NIE Networks have planned works to be carried out at this site to make the 33/11kV transformers reverse power capable during RP6 | No | No | Yes
Killealy Central | 54.6681 | -6.2006 | 33/11kV | ANTRIM MAIN | 2.101 | 24.53 | 35.9801 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 7.125 | 4.7105 | 0.05 | 2.3645 | 27.1745 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 164.2773 | 486.4411 | 486.4411 |  |  | Yes | No | No
Killinchy Central | 54.4728 | -5.6874 | 33/11kV | ROSEBANK MAIN | 0 | 0.77548 | 58.7959 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 0.33967 | 0 | 4.4103 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 0 | 0 |  |  | Yes | No | No
Killylea West | 54.3434 | -6.7966 | 33/11kV | DRUMNAKELLY MAIN | 1.8705 | 29.4942 | 0 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 0.31105 | 2.2741 | 0.036 | 0 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 190.4762 | 293.2286 | 370.4823 |  |  | No | Yes | No
Killyman Central | 54.4752 | -6.7357 | 33/11kV | DUNGANNON MAIN | 14.5203 | 13.7652 | 0 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 17.8125 | 3.0558 | 0.15 | 14.6067 | 21.2641 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 344.9074 | 344.9074 |  |  | Yes | No | No
Kilrea Central | 54.9623 | -6.5155 | 33/11kV | BALLYMENA RURAL | 0 | 0 | 60.7121 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 2.7334 | 0 | 2.0166 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 571.4286 | 571.4286 |  |  | Yes | No | No
Kircubbin East | 54.4897 | -5.5091 | 33/11kV | NEWTOWNARDS MAIN | 0.69719 | 3.4393 | 16.2015 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 2.2735 | 0.225 | 2.2515 | 19.7077 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 463.1257 | 571.4286 |  |  | Yes | No | No
Knockmore Central | 54.5078 | -6.0872 | 33/11kV | LISBURN MAIN | 2.6138 | 2.6138 | 26.3019 |  | 0.8 | 1.0621 | 0.39 | 0 | 11.1839 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 41.827 | 271.9371 | 486.1509 |  |  | No | Yes | Yes
Laganside | 54.5965 | -5.9174 | 33/11kV | CREGAGH MAIN | 11.4389 | 36.5916 | 4.9036 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 14.25 | 0.10725 | 0 | 14.1427 | 19.1827 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 190.4762 | 0 | 0 |  |  | Yes | No | No
Laragh Central | 54.5477 | -7.1923 | 33/11kV | OMAGH MAIN | 0 | 2.463 | 36.2426 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 2.0503 | 0.08 | 2.6197 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 170.5097 | 170.5097 |  |  | Yes | No | No
Larne North | 54.864 | -5.8191 | 33/11kV | LARNE MAIN | 7.6371 | 7.6371 | 0 |  | 0.82933 | 1.7641 | 0.044 | 0 | 10.8399 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 171.664 | 571.4286 | 571.4286 |  | NIE Networks have planned works to be carried out at this site to make the 33/11kV transformers reverse power capable during RP6 | No | Yes | Yes
Lenamore | 55.036 | -7.3206 | 33/11kV | SPRINGTOWN MAIN | 5.951 | 5.951 | 45.7163 |  | 7.6 | 1.8407 | 0 | 5.7593 | 16.8507 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 176.6598 | 571.4286 | 571.4286 |  |  | Yes | No | No
Limavady Town | 55.0501 | -6.9418 | 33/11kV | LIMAVADY MAIN | 4.8857 | 23.62 | 20.5435 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 11.4 | 3.6001 | 0 | 7.7999 | 14.755 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 4.88 | 4.88 |  |  | Yes | No | No
Lisburn North | 54.5335 | -6.0394 | 33/11kV | LISBURN MAIN | 0 | 4.9973 | 26.3019 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 1.047 | 0.45157 | 0 | 0.59547 | 4.9787 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 63.0827 | 271.9371 | 486.1509 |  | NIE Networks have planned works to be carried out at this site to make the 33/11kV transformers reverse power capable during RP6 | No | Yes | Yes
Lisburn South | 54.5109 | -6.0347 | 33/11kV | FINAGHY MAIN | 7.1993 | 9.7377 | 13.7038 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 0.93539 | 0.60164 | 0.088 | 0.24575 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 190.4762 | 118.7086 | 118.7086 |  |  | No | Yes | Yes
Lisburn West | 54.5138 | -6.0572 | 33/11kV | LISBURN MAIN | 9.986 | 1.357 | 26.3019 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 1.1216 | 0.39452 | 0.11 | 0.61704 | 18.5413 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 190.4762 | 271.9371 | 486.1509 |  | NIE Networks have planned works to be carried out at this site to make the 33/11kV transformers reverse power capable during RP6 | No | Yes | Yes
Lisnaskea Central | 54.2585 | -7.4501 | 33/11kV | ENNISKILLEN MAIN | 3.8269 | 3.8269 | 28.5689 |  | 7.125 | 2.4362 | 0 | 4.6888 | 1.2388 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 205.8194 | 423.872 |  |  | Yes | No | No
Lurgan East | 54.4594 | -6.2852 | 33/11kV | WARINGSTOWN MAIN | 5.8355 | 5.8355 | 14.4216 |  | 2.7081 | 1.472 | 0.1015 | 1.1345 | 11.0265 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. New tapchangers required to make the site reverse power capable. | 190.4762 | 443.6731 | 443.6731 |  | NIE Networks have planned works to be carried out at this site to make the 33/11kV transformers reverse power capable during RP6 | No | Yes | No
Maghera North | 54.8494 | -6.6757 | 33/11kV | CREAGH MAIN | 1.2629 | 9.0061 | 8.5217 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 7.125 | 3.6415 | 0 | 3.4835 | 29.7211 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 121.0339 | 382.2171 | 571.4286 |  |  | Yes | No | No
Magherafelt West | 54.7607 | -6.6253 | 33/11kV | CREAGH MAIN | 10.6454 | 10.6454 | 8.5217 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 11.4 | 3.4186 | 0.15 | 7.8315 | 29.7211 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 382.2171 | 571.4286 |  |  | Yes | No | No
Magilligan Central | 55.1746 | -6.944 | 33/11kV | LIMAVADY MAIN |  |  | 20.5435 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 0.24492 | 0 | 4.5051 | 14.755 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 4.88 | 4.88 |  |  | Yes | No | No
Mallusk | 54.6743 | -5.9856 | 33/6.6kV | GLENGORMLEY MAIN | 0 | 15.8402 | 20.7622 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 17.8125 | 0.24418 | 0 | 17.5683 | 15.1658 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The transformers at this substation are reverse power capable. | 114.2857 | 322.1029 | 322.1029 |  |  | Yes | No | No
Markethill Central | 54.2886 | -6.5142 | 33/11kV | DRUMNAKELLY MAIN | 0.6668 | 29.4942 | 0 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 1.2214 | 0 | 3.5286 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 293.2286 | 370.4823 |  |  | Yes | No | No
Maydown | 55.0289 | -7.2562 | 33/11kV | COOLKEERAGH MAIN | 8.7704 | 8.7704 | 57.5972 |  | 0.49345 | 0.94792 | 0 | 0 | 17.8906 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. New tapchangers required to make the site reverse power capable. | 190.4762 | 571.4286 | 571.4286 |  |  | No | Yes | No
Monbrief | 54.45 | -6.3453 | 33/11kV | WARINGSTOWN MAIN | 10.7097 | 19.3815 | 14.4216 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 1.7805 | 1.3898 | 0 | 0.3907 | 15.4382 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 59.9992 | 443.6731 | 443.6731 |  |  | No | Yes | Yes
Monkstown | 54.6853 | -5.9176 | 33/6.6kV | CARNMONEY MAIN | 0 | 0 | 23.9527 |  | 17.8125 | 2.7216 | 0 | 15.0909 | 10.2284 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The transformers at this substation are reverse power capable. | 114.2857 | 148.9166 | 148.9166 |  |  | Yes | No | No
Moscow Road | 54.6227 | -5.8738 | 33/11kV | KNOCK MAIN | 6.534 | 18.1225 | 16.9963 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 1.0136 | 0.03375 | 0.08 | 0.89981 | 12.3562 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 190.4762 | 571.4286 | 571.4286 |  |  | No | No | Yes
Mountpottinger | 54.5951 | -5.9006 | 33/6.6kV | CREGAGH MAIN | 5.8456 | 36.5916 | 4.9036 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 11.875 | 0.17806 | 0 | 11.6969 | 13.3919 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The transformers at this substation are reverse power capable. | 114.2857 | 0 | 0 |  |  | Yes | No | No
Moy Park | 54.4948 | -6.7408 | 33/11kV | DUNGANNON MAIN | 5.4257 | 13.7652 | 0 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 11.875 | 0.25264 | 0 | 11.6224 | 21.2641 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 176.8229 | 344.9074 | 344.9074 |  |  | Yes | No | No
Mulhouse Road | 54.5948 | -5.9512 | 33/6.6kV | DONEGALL MAIN (SOUTH) | 1.924 | 1.924 | 23.3305 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 11.4 | 0.10204 | 0 | 11.298 | 13.598 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The transformers at this substation are reverse power capable. | 114.2857 | 571.4286 | 571.4286 |  |  | Yes | No | No
Mullaghglass | 54.5618 | -6.0586 | 33/11kV | LISBURN MAIN | 0 | 4.9973 | 26.3019 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 3.8 | 3.1547 | 0.699 | 0 | 4.9787 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 271.9371 | 486.1509 |  |  | Yes | No | No
Newbuildings | 54.957 | -7.3584 | 33/11kV | LISAGHMORE MAIN | 1.6195 | 1.6195 | 4.1257 |  | 5.9375 | 0.81664 | 0 | 5.1209 | 3.3244 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 342.9029 | 448.3589 |  |  | Yes | No | No
Newcastle North | 54.2185 | -5.889 | 33/11kV | BALLYNAHINCH MAIN | 7.6915 | 0 | 11.7745 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 1.3456 | 1.2609 | 0.898 | 0 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 190.4762 | 468.8286 | 560.7223 |  |  | No | No | Yes
Newpark | 54.7144 | -6.1756 | 33/11kV | ANTRIM MAIN | 9.5777 | 9.5777 | 35.9801 |  | 1.3706 | 2.0053 | 0 | 0 | 22.5339 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 190.4762 | 486.4411 | 486.4411 |  |  | No | Yes | Yes
Newry East | 54.183 | -6.3247 | 33/11kV | NEWRY MAIN | 1.3271 | 1.3271 | 6.2341 |  | 11.875 | 0.41207 | 0 | 11.4629 | 23.7601 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 378.3829 | 567.9451 |  |  | Yes | No | No
Newry North | 54.1948 | -6.3488 | 33/11kV | NEWRY MAIN | 11.3329 | 11.0635 | 6.2341 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 1.9273 | 0.71656 | 1.4442 | 0 | 22.5663 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. New tapchangers required to make the site reverse power capable. | 190.4762 | 378.3829 | 567.9451 |  |  | No | Yes | No
Newry South | 54.1652 | -6.3386 | 33/11kV | NEWRY MAIN | 1.8287 | 1.8287 | 6.2341 |  | 7.6 | 1.1028 | 0.41 | 6.0872 | 20.2138 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 378.3829 | 567.9451 |  |  | Yes | No | No
Newtownards Central | 54.587 | -5.7017 | 33/11kV | NEWTOWNARDS MAIN | 7.5417 | 7.4532 | 16.2015 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 1.443 | 3.0517 | 0 | 0 | 21.8602 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. New tapchangers required to make the site reverse power capable. | 46.4488 | 463.1257 | 571.4286 |  |  | No | Yes | No
Newtownbreda | 54.5499 | -5.9235 | 33/6.6kV | CREGAGH MAIN | 3.0217 | 3.0217 | 4.9036 |  | 11.875 | 0.64814 | 0 | 11.2269 | 12.5519 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The transformers at this substation are reverse power capable. | 114.2857 | 0 | 0 |  |  | Yes | No | No
Newtownhamilton East | 54.1908 | -6.5655 | 33/11kV | NEWRY MAIN | 0 | 0 | 6.2341 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 2.142 | 0 | 2.608 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 378.3829 | 567.9451 |  |  | Yes | No | No
North Foreshore | 54.6257 | -5.8969 | 33/6.6kV | BELFAST NORTH MAIN | 9.7839 | 73.7462 | 29.8706 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 0.484 | 0.131 | 0 | 0.353 | 19.149 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 114.2857 | 428.6011 | 571.4286 |  |  | No | No | Yes
Omagh East | 54.6083 | -7.2833 | 33/11kV | OMAGH MAIN | 8.281 | 8.281 | 36.2426 |  | 1.126 | 2.5702 | 0.19 | 0 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 163.1337 | 170.5097 | 170.5097 |  |  | No | Yes | Yes
Omagh South | 54.5823 | -7.2817 | 33/11kV | OMAGH MAIN | 0 | 0 | 36.2426 |  | 9.5 | 0.49156 | 0 | 9.0084 | 23.9404 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 151.9863 | 170.5097 | 170.5097 |  |  | Yes | No | No
Omagh West | 54.5984 | -7.3135 | 33/11kV | OMAGH MAIN | 5.2402 | 5.2402 | 36.2426 |  | 1.7531 | 1.2714 | 0.05 | 0.43169 | 11.6738 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 190.4762 | 170.5097 | 170.5097 |  |  | No | Yes | Yes
Parkhall | 54.7156 | -6.2089 | 33/11kV | ANTRIM MAIN | 3.8827 | 3.8827 | 35.9801 |  | 1.8968 | 1.1137 | 0.317 | 0.4661 | 20.8123 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 190.4762 | 486.4411 | 486.4411 |  |  | No | No | Yes
Plumbridge Central | 54.7682 | -7.2609 | 33/11kV | STRABANE MAIN | 0 | 0 | 0 |  | 3.8 | 0.75867 | 0 | 3.0413 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 205.2057 | 571.4286 |  |  | Yes | No | No
Pomeroy | 54.5998 | -6.9487 | 33/11kV | OMAGH MAIN | 0 | 0 | 36.2426 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 2.1588 | 0.45 | 2.1412 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 170.5097 | 170.5097 |  |  | Yes | No | No
Portadown North | 54.428 | -6.4391 | 33/11kV | DRUMNAKELLY MAIN | 15.9711 | 0 | 0 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 1.2016 | 1.1642 | 0.156 | 0 | 30.3325 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 36.1257 | 293.2286 | 370.4823 |  | NIE Networks have planned works to be carried out at this site to make the 33/11kV transformers reverse power capable during RP6 | No | Yes | Yes
Portadown South | 54.4092 | -6.4553 | 33/11kV | DRUMNAKELLY MAIN | 0.30513 | 0.30513 | 0 |  | 1.1108 | 1.5664 | 0.2039 | 0 | 17.0312 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. New tapchangers required to make the site reverse power capable. | 190.4762 | 293.2286 | 370.4823 |  | NIE Networks have planned works to be carried out at this site to make the 33/11kV transformers reverse power capable during RP6 | No | Yes | No
Portglenone Central | 54.8742 | -6.4615 | 33/11kV | BALLYMENA RURAL | 0 | 22.4798 | 60.7121 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 1.7128 | 0.1 | 2.9372 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 571.4286 | 571.4286 |  |  | Yes | No | No
Portstewart South | 55.178 | -6.6853 | 33/11kV | LOGUESTOWN MAIN | 8.4525 | 8.4525 | 9.4204 |  | 1.4262 | 2.7584 | 0.066 | 0 | 20.7508 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 190.4762 | 571.4286 | 571.4286 |  |  | No | Yes | Yes
Poyntzpass Central | 54.2911 | -6.3747 | 33/11kV | BANBRIDGE MAIN | 0 | 0 | 31.2058 |  | 4.75 | 2.9833 | 0 | 1.7667 | 1.441 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 398.6571 | 491.7143 |  |  | Yes | No | No
Queens Road | 54.6095 | -5.9051 | 33/6.6kV | CREGAGH MAIN | 7.2725 | 36.5916 | 4.9036 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 11.4 | 0 | 0 | 11.4 | 23 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The transformers at this substation are reverse power capable. | 114.2857 | 0 | 0 |  |  | Yes | No | No
Randalstown Central | 54.7528 | -6.3172 | 33/11kV | ANTRIM MAIN | 9.2473 | 9.2473 | 35.9801 |  | 11.875 | 2.0311 | 0 | 9.8439 | 9.6539 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 486.4411 | 486.4411 |  |  | Yes | No | No
Rathcoole | 54.667 | -5.9368 | 33/6.6kV | CARNMONEY MAIN | 7.946 | 7.946 | 23.9527 |  | 11.875 | 0.20715 | 0 | 11.6678 | 15.2928 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The transformers at this substation are reverse power capable. | 80.9947 | 148.9166 | 148.9166 |  |  | Yes | No | No
Rathfriland Central | 54.2333 | -6.147 | 33/11kV | BANBRIDGE MAIN | 7.6907 | 7.6907 | 31.2058 |  | 11.875 | 2.4454 | 0 | 9.4296 | 0.38658 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 398.6571 | 491.7143 |  |  | Yes | No | No
Richhill Central | 54.3851 | -6.5391 | 33/11kV | DRUMNAKELLY MAIN | 0 | 29.4942 | 0 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 3.8 | 2.7462 | 0 | 1.0538 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 293.2286 | 370.4823 |  |  | Yes | No | No
Rostrevor Central | 54.0957 | -6.1895 | 33/11kV | NEWRY MAIN | 0 | 3.2998 | 6.2341 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 2.85 | 0.13728 | 0 | 2.7127 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 190.4762 | 378.3829 | 567.9451 |  |  | Yes | No | No
Roughfort Central | 54.6873 | -6.0202 | 33/11kV | GLENGORMLEY MAIN | 10.078 | 15.8402 | 20.7622 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 11.875 | 4.2054 | 1.748 | 5.9216 | 11.7758 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 175.1756 | 322.1029 | 322.1029 |  |  | Yes | No | No
Seaforde Central | 54.3061 | -5.8351 | 33/11kV | BALLYNAHINCH MAIN | 3.1743 | 18.0713 | 11.7745 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 1.6322 | 0.25 | 2.8678 | 4.5428 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 190.4762 | 468.8286 | 560.7223 |  |  | Yes | No | No
Seagoe Central | 54.4426 | -6.4293 | 33/11kV | DRUMNAKELLY MAIN | 8.2654 | 0 | 0 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 0.85416 | 0.21038 | 2.655 | 0 | 30.3325 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 190.4762 | 293.2286 | 370.4823 |  | NIE Networks have planned works to be carried out at this site to make the 33/11kV transformers reverse power capable during RP6 | No | Yes | Yes
Shankill | 54.6083 | -5.9522 | 33/6.6kV | DONEGALL MAIN (SOUTH) | 5.6762 | 5.6762 | 23.3305 |  | 0.82525 | 0.3231 | 0 | 0.50215 | 13.0869 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 98.6665 | 571.4286 | 571.4286 |  |  | No | No | Yes
Shrigley Central | 54.4083 | -5.6645 | 33/11kV | BALLYNAHINCH MAIN | 0 | 0.77548 | 11.7745 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 5.9375 | 0.7921 | 0 | 5.1454 | 1.7944 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. New tapchangers required to make the site reverse power capable. | 190.4762 | 468.8286 | 560.7223 |  |  | Yes | No | No
Silverbridge West | 54.0992 | -6.5371 | 33/11kV | NEWRY MAIN | 8.6604 | 0 | 6.2341 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 11.875 | 1.419 | 0 | 10.456 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 378.3829 | 567.9451 |  |  | Yes | No | No
Sion Mills | 54.7856 | -7.4648 | 33/11kV | STRABANE MAIN | 1.8132 | 3.5036 | 0 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 1.9915 | 0 | 2.7585 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 205.2057 | 571.4286 |  |  | Yes | No | No
Skegoneill Street | 54.622 | -5.9214 | 33/6.6kV | BELFAST NORTH MAIN | 10.983 | 73.7462 | 29.8706 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 7.6 | 5.1806 | 0 | 2.4194 | 5.8144 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The transformers at this substation are reverse power capable. | 114.2857 | 428.6011 | 571.4286 |  |  | Yes | No | No
South Central | 54.5885 | -5.934 | 33/6.6kV | DONEGALL MAIN (NORTH) | 1.6187 | 1.6187 | 15.4556 |  | 17.8125 | 0.109 | 0 | 17.7035 | 24.791 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The transformers at this substation are reverse power capable. | 45.147 | 571.4286 | 571.4286 |  |  | Yes | No | No
Springfield | 54.6008 | -5.964 | 33/6.6kV | DONEGALL MAIN (SOUTH) | 8.489 | 8.489 | 23.3305 |  | 11.875 | 0.1693 | 0 | 11.7057 | 13.3807 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The transformers at this substation are reverse power capable. | 19.8935 | 571.4286 | 571.4286 |  |  | Yes | No | No
Sprucefield | 54.4943 | -6.0542 | 33/11kV | LISBURN MAIN | 8.1183 | 45.3778 | 26.3019 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 1.7841 | 3.1319 | 0.252 | 0 | 26.8736 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 190.4762 | 271.9371 | 486.1509 |  | NIE Networks have planned works to be carried out at this site to make the 33/11kV transformers reverse power capable during RP6 | No | Yes | Yes
Strand Road | 55.0013 | -7.3217 | 33/11kV | LISAGHMORE MAIN | 10.9499 | 10.9499 | 4.1257 |  | 2.1539 | 0.43214 | 0 | 1.7217 | 22.8559 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 190.4762 | 342.9029 | 448.3589 |  |  | No | Yes | Yes
Sydenham | 54.608 | -5.873 | 33/6.6kV | KNOCK MAIN | 0 | 18.1225 | 16.9963 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 11.875 | 0.21091 | 0 | 11.6641 | 15.2191 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The transformers at this substation are reverse power capable. | 114.1797 | 571.4286 | 571.4286 |  |  | Yes | No | No
Talbot Street | 54.6029 | -5.9264 | 33/6.6kV | BELFAST CENTRAL MAIN | 6.8318 | 6.8318 | 35.2124 |  | 1.0748 | 0.09678 | 0 | 0.97797 | 23.8432 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 114.2857 | 456.4137 | 456.4137 |  |  | No | No | Yes
Tandragee East | 54.3566 | -6.399 | 33/11kV | DRUMNAKELLY MAIN | 6.4423 | 23.8328 | 0 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 11.875 | 1.5271 | 0 | 10.3479 | 3.9931 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 118.4114 | 293.2286 | 370.4823 |  | NIE Networks have planned works to be carried out at this site to make the 33/11kV transformers reverse power capable during RP6 | Yes | No | No
Toome East | 54.7403 | -6.3958 | 33/11kV | CREAGH MAIN | 0 | 0 | 8.5217 |  | 4.75 | 2.0732 | 0 | 2.6768 | 0.80323 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 382.2171 | 571.4286 |  |  | Yes | No | No
Tullyaran Central | 54.5524 | -6.8498 | 33/11kV | DUNGANNON MAIN | 0.80526 | 34.3935 | 0 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 2.9839 | 0.06 | 1.7061 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 344.9074 | 344.9074 |  |  | Yes | No | No
Tullygoonigan | 54.3905 | -6.6668 | 33/11kV | DRUMNAKELLY MAIN | 1.1639 | 29.4942 | 0 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 4.75 | 1.1118 | 0 | 3.6382 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 293.2286 | 370.4823 |  |  | Yes | No | No
Tullyvannon | 54.494 | -6.9607 | 33/11kV | DUNGANNON MAIN | 0 | 0 | 0 |  | 9.5 | 0.496 | 0 | 9.004 | 13.4674 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 344.9074 | 344.9074 |  |  | Yes | No | No
Ulster Chipboard | 55.1095 | -6.6555 | 33/11kV | COLERAINE MAIN | 0 | 0 | 18.827 |  | 3.8 | 0.494 | 0 | 3.306 | 11.9765 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 160.771 | 320.9086 | 408.576 |  |  | Yes | No | No
Warrenpoint North | 54.1088 | -6.2519 | 33/11kV | NEWRY MAIN | 6.0644 | 14.512 | 6.2341 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 11.875 | 0.96582 | 0 | 10.9092 | 5.1672 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 105.9703 | 378.3829 | 567.9451 |  |  | Yes | No | No
West Central | 54.5999 | -5.9415 | 33/6.6kV | BELFAST CENTRAL MAIN | 5.6468 | 5.6468 | 35.2124 |  | 0.81176 | 0.2195 | 0.21 | 0.38226 | 23.4005 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 76.9915 | 456.4137 | 456.4137 |  |  | No | No | Yes
Whitehouse | 54.6536 | -5.9229 | 33/6.6kV | BELFAST NORTH MAIN | 7.6328 | 73.7462 | 29.8706 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 1.6377 | 0.21344 | 0 | 1.4243 | 14.0966 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 114.2857 | 428.6011 | 571.4286 |  |  | No | No | Yes
Woodside Road | 54.8735 | -6.2349 | 33/11kV | BALLYMENA TOWN | 0.44855 | 4.7071 | 27.0009 | As this substation is part of a 33kV meshed network; capacity stated under Upstream Demand Headroom (Distribution Network) will be shared with adjacent primary substations. | 11.875 | 4.434 | 0.199 | 7.242 | 12.8803 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. As this substation is part of a 33kV meshed network; capacity stated under Upstream Generation Headroom (Distribution Network) will be shared with adjacent primary substations. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 0 | 506.3543 |  |  | Yes | No | No
Woodville | 54.4711 | -6.3334 | 33/11kV | WARINGSTOWN MAIN | 8.0114 | 8.0114 | 14.4216 |  | 0.89166 | 1.1898 | 0 | 0 | 6.5591 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 180.5722 | 443.6731 | 443.6731 |  | NIE Networks have planned works to be carried out at this site to make the 33/11kV transformers reverse power capable during RP6 | No | Yes | Yes
East Central | 54.5966 | -5.9259 | 33/11kV | BELFAST CENTRAL MAIN | 0 | 21.5478 | 35.2124 | Available Upstream Demand Headroom (Distribution Network) will be shared with East Central 33/6.6kV substation. | 17.8125 | 0 | 0 | 17.8125 | 33.4 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. Available Upstream Generation Headroom (Distribution Network) will be shared with East Central 33/6.6kV substation. The 33/11kV transformers at this substation are reverse power capable. | 178.0571 | 456.4137 | 456.4137 |  |  | Yes | No | No
East Central | 54.5966 | -5.9259 | 33/6.6kV | BELFAST CENTRAL MAIN | 8.6368 | 21.5478 | 35.2124 | Available Upstream Demand Headroom (Distribution Network) will be shared with East Central 33/11kV substation. | 11.875 | 0 | 0 | 11.875 | 33.4 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. Available Upstream Generation Headroom (Distribution Network) will be shared with East Central 33/11kV substation. The transformers at this substation are reverse power capable. | 107.2981 | 456.4137 | 456.4137 |  |  | Yes | No | No
King Street | 54.5985 | -5.9356 | 33/11kV | BELFAST CENTRAL MAIN | 14.0025 | 14.0025 | 35.2124 |  | 1.366 | 0.06748 | 0.558 | 0.74055 | 14.3745 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. The 33/11kV transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 190.4762 | 456.4137 | 456.4137 |  |  | No | No | Yes
King Street | 54.5985 | -5.9356 | 33/6.6kV | BELFAST CENTRAL MAIN | 6.2047 | 6.2047 | 35.2124 |  | 14.25 | 0.06748 | 0.4 | 13.7825 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The transformers at this substation are reverse power capable. | 76.5051 | 456.4137 | 456.4137 |  |  | Yes | No | No
Ormeau | 54.5745 | -5.9239 | 33/11kV | CREGAGH MAIN | 5.3372 | 5.3372 | 4.9036 |  | 17.8125 | 0.05636 | 0 | 17.7561 | 24.2106 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 0 | 0 |  |  | Yes | No | No
Ormeau | 54.5745 | -5.9239 | 33/6.6kV | CREGAGH MAIN | 9.3585 | 9.3585 | 4.9036 |  | 17.8125 | 0.16484 | 0 | 17.6477 | 23.8352 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The transformers at this substation are reverse power capable. | 114.2857 | 0 | 0 |  |  | Yes | No | No
Malone | 54.5814 | -5.9494 | 33/11kV | DONEGALL MAIN (SOUTH) | 0.71416 | 0 | 23.3305 | Available Upstream Demand Headroom (Distribution Network) will be shared with Malone 33/6.6kV substation. | 14.25 | 0.345 | 0 | 13.905 | 21.9782 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. Available Upstream Generation Headroom (Distribution Network) will be shared with Malone 33/6.6kV substation. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 571.4286 | 571.4286 |  |  | Yes | No | No
Malone | 54.5814 | -5.9494 | 33/6.6kV | DONEGALL MAIN (SOUTH) | 0.04651 | 0 | 23.3305 | Available Upstream Demand Headroom (Distribution Network) will be shared with Malone 33/11kV substation. | 0 | 0.24418 | 0 | 0 | 21.9658 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. Available Upstream Generation Headroom (Distribution Network) will be shared with Malone 33/11kV substation. The transformers at this substation are reverse power capable. | 98.1541 | 571.4286 | 571.4286 |  |  | Yes | No | No

## BSP
Bulk Supply Point | Latitude | Longitude | BSP Voltage Domain | Transformer Demand Headroom | Demand Comment | Substation Generation Capacity | Connected Generation | Committed (Not Yet Connected) | Substation Generation Headroom | Generation Comment | Substation Fault Level Headroom | Fault Level Comment | Statement of Works
AGHYOULE MAIN | 54.1627 | -7.585 | 110/33kV | 6.9382 |  |  | 70.409 | 19.87 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 347.0789
BALLYMENA RURAL | 54.85 | -6.2853 | 110/33kV | 60.7121 |  |  | 45.1335 | 35.41 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 571.4286
BALLYNAHINCH MAIN | 54.3907 | -5.8783 | 110/33kV | 11.7745 |  |  | 18.5876 | 19.874 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 560.7223
COLERAINE MAIN | 55.1091 | -6.6874 | 110/33kV | 18.827 |  |  | 124.2009 | 0.738 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 408.576
COOLKEERAGH MAIN | 55.0426 | -7.2451 | 110/33kV | 57.5972 |  |  | 3.1909 | 17.605 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 571.4286
DONEGALL MAIN (NORTH) | 54.5914 | -5.9528 | 110/33kV | 15.4556 |  |  | 1.2812 | 0 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 571.4286
DONEGALL MAIN (SOUTH) | 54.5906 | -5.9543 | 110/33kV | 23.3305 |  |  | 2.2014 | 0.3 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 571.4286
DRUMNAKELLY MAIN | 54.4019 | -6.4546 | 110/33kV | 0 |  |  | 24.8126 | 19.5615 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 370.4823
EDEN MAIN | 54.7377 | -5.7828 | 110/33kV | 0 |  |  | 8.8877 | 2.157 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 0
FINAGHY MAIN | 54.57 | -5.9946 | 110/33kV | 13.7038 |  |  | 2.4587 | 0.8 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 118.7086
LARNE MAIN | 54.8477 | -5.8554 | 110/33kV | 0 |  |  | 31.1189 | 16.5635 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 571.4286
LIMAVADY MAIN | 55.0242 | -6.9159 | 110/33kV | 20.5435 |  |  | 45.5603 | 0.5 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 4.88
LISAGHMORE MAIN | 54.9806 | -7.3048 | 110/33kV | 4.1257 |  |  | 20.6879 | 0.056 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 448.3589
LISBURN MAIN | 54.5212 | -6.0904 | 110/33kV | 26.3019 |  |  | 94.3175 | 8.751 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 486.1509
NEWRY MAIN | 54.1791 | -6.3199 | 110/33kV | 6.2341 |  |  | 13.8777 | 2.3342 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 567.9451
OMAGH MAIN | 54.5779 | -7.2809 | 110/33kV | 36.2426 |  |  | 144.2873 | 1.767 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 170.5097
ROSEBANK MAIN | 54.5756 | -5.868 | 110/33kV | 58.7959 |  |  | 25.549 | 4 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 0
MAGHERAKEEL MAIN (CLUSTER) | 54.6538 | -7.7323 | 110/33kV | 0 | Cluster substation for generation only - No demand connection available. | 138 | 119.2 | 18.8 | 0 | For further information - please check visit this link: https://www.nienetworks.co.uk/connections/generation-connections/generation-useful-resources
GORT MAIN (CLUSTER) | 54.4856 | -7.1168 | 110/33kV | 0 | Cluster substation for generation only - No demand connection available. | 90 | 67.5 | 22.5 | 0 | For further information - please check visit this link: https://www.nienetworks.co.uk/connections/generation-connections/generation-useful-resources
TREMOGE MAIN (CLUSTER) | 54.6065 | -6.9675 | 110/33kV | 0 | Cluster substation for generation only - No demand connection available. | 90 | 77.15 | 12.85 | 0 | For further information - please check visit this link: https://www.nienetworks.co.uk/connections/generation-connections/generation-useful-resources
RASHARKIN MAIN (CLUSTER) | 54.9653 | -6.4958 | 110/33kV | 0 | Cluster substation for generation only - No demand connection available. | 90 | 89.82 | 21.5 | 0 | For further information - please check visit this link: https://www.nienetworks.co.uk/connections/generation-connections/generation-useful-resources
CURRAGHMULKIN (DRUMQUIN) MAIN (CLUSTER) | 54.5752 | -7.4861 | 110/33kV | 0 | Cluster substation for generation only - No demand connection available. | 90 | 67.9 | 0 | 22.1 | For further information - please check visit this link: https://www.nienetworks.co.uk/connections/generation-connections/generation-useful-resources
AGIVEY (GARVAGH) MAIN (CLUSTER) | 55.0006 | -6.6532 | 110/33kV | 0 | Cluster substation for generation only - No demand connection available. | 90 | 70.3 | 67 | 0 | For further information - please check visit this link: https://www.nienetworks.co.uk/connections/generation-connections/generation-useful-resources
KELLS MAIN (CLUSTER) | 54.8015 | -6.1674 | 110/33kV | 0 | Cluster substation for generation only - No demand connection available. | 90 | 0 | 65.6 | 24.4 | For further information - please check visit this link: https://www.nienetworks.co.uk/connections/generation-connections/generation-useful-resources

## BSP-Primary-combined
Bulk Supply Point | Latitude | Longitude | BSP Voltage Domain | Primary Voltage Domain | Transformer Demand Headroom (Bulk Supply Point) | Demand Comment | Substation Generation Capacity | Connected Generation | Committed (Not Yet Connected) | Substation Generation Headroom (Bulk Supply Point) | Generation Comment | Substation Fault Level Headroom (Bulk Supply Point) | Fault Level Comment | Statement of Works | Transformer Demand Headroom (Primary) | Upstream Demand Headroom (Bulk Supply Point) | Demand Comment.1 | Substation Generation Capacity (Primary) | Connected Generation (Primary) | Committed (Not Yet Connected).1 | Substation Generation Headroom (Primary) | Upstream Generation Headroom (BSP) | Generation Comment.1 | Substation Fault Level Headroom (Primary) | Upstream Fault Level Headroom (BSP) | Fault Level Comment.1 | Statement of Works.1 | 33/11kV Transformers Reverse Power Capable? | New 33/11kV Tapchanger Required? | New 33/11kV Relay Required?
ANTRIM MAIN | 54.7277 | -6.2209 | 110/33kV | 33/11kV | 35.9801 |  |  | 15.8561 | 12.757 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 486.4411 |  |  | 10.1921 | 35.9801 |  | 11.4 | 5.9955 | 4.8 | 0.60451 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 114.6469 | 486.4411 |  |  | Yes | No | No
BALLYMENA TOWN | 54.8512 | -6.2853 | 110/33kV | 33/11kV | 27.0009 |  |  | 17.2931 | 0.934 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 506.3543 |  |  | 5.055 | 27.0009 |  | 1.1 | 0.65 | 0.5 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 50.8975 | 506.3543 |  | NIE Networks have approved works to be carried out at this site to make the 33/11kV transformers reverse power capable during RP6 | Yes | No | No
BANBRIDGE MAIN | 54.344 | -6.2458 | 110/33kV | 33/11kV | 31.2058 |  |  | 14.6846 | 128.853 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 491.7143 |  |  | 6.6801 | 31.2058 |  | 17.8125 | 4.6865 | 0 | 14.25 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 24.5135 | 491.7143 |  |  | Yes | No | No
BELFAST CENTRAL MAIN | 54.6046 | -5.9245 | 110/33kV | 33/11kV | 35.2124 |  |  | 0.54024 | 1.721 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 456.4137 |  |  | 10.2305 | 35.2124 |  | 1.2764 | 0.089 | 0.553 | 0.63441 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 190.4762 | 456.4137 |  |  | No | No | Yes
BELFAST NORTH MAIN | 54.6111 | -5.9193 | 110/33kV | 33/6.6kV | 29.8706 |  |  | 16.8534 | 6.442 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 571.4286 |  |  | 5.5031 | 29.8706 |  | 0.6 | 0.13618 | 0.022 | 0.44182 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 114.2857 | 571.4286 |  |  | No | No | Yes
CARNMONEY MAIN | 54.6867 | -5.9537 | 110/33kV | 33/6.6kV | 23.9527 |  |  | 17.0716 | 30.236 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 148.9166 |  |  | 4.5578 | 23.9527 |  | 0.80115 | 0.34294 | 0.036 | 0.42221 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 114.2857 | 148.9166 |  |  | No | No | Yes
CREGAGH MAIN | 54.5824 | -5.8959 | 110/33kV | 33/6.6kV | 4.9036 |  |  | 1.6814 | 0 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 0 |  |  | 16.7929 | 4.9036 |  | 71.25 | 0.36478 | 0 | 70.8852 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The transformers at this substation are reverse power capable. | 49.264 | 0 |  |  | Yes | No | No
CREAGH MAIN | 54.7612 | -6.4927 | 110/33kV | 33/11kV | 8.5217 |  |  | 24.8756 | 3.448 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 571.4286 |  |  | 8.1699 | 8.5217 |  | 0.25015 | 0.342 | 0.04 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are not reverse power capable. New relays required to make the site reverse power capable. | 190.4762 | 571.4286 |  |  | No | No | Yes
DUNGANNON MAIN | 54.5331 | -6.7496 | 110/33kV | 33/11kV | 0 |  |  | 45.5507 | 6.419 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 344.9074 |  |  | 8.2214 | 0 |  | 7.6 | 3.1614 | 4.989 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 159.824 | 344.9074 |  |  | Yes | No | No
ENNISKILLEN MAIN | 54.3671 | -7.6326 | 110/33kV | 33/11kV | 28.5689 |  |  | 37.2666 | 15.25 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 423.872 |  |  | 8.6667 | 28.5689 |  | 11.875 | 2.1506 | 0 | 9.7244 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 158.4457 | 423.872 |  |  | Yes | No | No
GLENGORMLEY MAIN | 54.6762 | -5.9661 | 110/33kV | 33/6.6kV | 20.7622 |  |  | 12.3329 | 1.863 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 322.1029 |  |  | 13 | 20.7622 |  | 1.1148 | 0.36334 | 0.115 | 0.63649 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 108.5888 | 322.1029 |  |  | No | Yes | Yes
KNOCK MAIN | 54.5945 | -5.8563 | 110/33kV | 33/6.6kV | 16.9963 |  |  | 2.731 | 0.12 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 571.4286 |  |  | 8.3688 | 16.9963 |  | 17.8125 | 0.55162 | 0 | 17.2609 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The transformers at this substation are reverse power capable. | 70.6199 | 571.4286 |  |  | Yes | No | No
LOGUESTOWN MAIN | 55.1478 | -6.6562 | 110/33kV | 33/11kV | 9.4204 |  |  | 10.9496 | 13.6005 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 571.4286 |  |  | 8.175 | 9.4204 |  | 7.125 | 4.6625 | 0 | 2.4625 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 571.4286 |  |  | Yes | No | No
NEWTOWNARDS MAIN | 54.6026 | -5.6775 | 110/33kV | 33/11kV | 16.2015 |  |  | 17.574 | 0.7525 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 571.4286 |  |  | 7.0699 | 16.2015 |  | 11.4 | 2.5887 | 0 | 8.8113 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 166.1646 | 571.4286 |  |  | Yes | No | No
RATHGAEL MAIN | 54.6466 | -5.6724 | 110/33kV | 33/11kV | 28.0689 |  |  | 5.8082 | 0.415 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 345.2549 |  |  | 12.5295 | 28.0689 |  | 1.5846 | 1.7067 | 0.415 | 0 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 190.4762 | 345.2549 |  |  | No | Yes | Yes
SPRINGTOWN MAIN | 55.0197 | -7.3335 | 110/33kV | 33/11kV | 45.7163 |  |  | 4.3979 | 0 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 571.4286 |  |  | 15.783 | 45.7163 |  | 17.8125 | 0.70119 | 0 | 17.1113 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 190.4762 | 571.4286 |  |  | Yes | No | No
STRABANE MAIN | 54.8525 | -7.4307 | 110/33kV | 33/11kV | 0 |  |  | 51.6109 | 0.025 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 571.4286 |  |  | 0 | 0 |  | 11.875 | 7.3093 | 0 | 4.5657 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are reverse power capable. | 127.2358 | 571.4286 |  |  | Yes | No | No
WARINGSTOWN MAIN | 54.4504 | -6.3079 | 110/33kV | 33/11kV | 14.4216 |  |  | 5.4228 | 9.3715 |  | BSP Substation Generation Headroom is the responsibility of SONI. Contact NIE Networks or SONI for more information. | 443.6731 |  |  | 11.3828 | 14.4216 |  | 0.70414 | 0.64601 | 0 | 0.058135 |  | Upstream Generation Headroom (BSP) is the responsibility of SONI. Contact NIE Networks or SONI for more information. The 33/11kV transformers at this substation are not reverse power capable. New tapchangers and relays required to make the site reverse power capable. | 190.4762 | 443.6731 |  |  | No | Yes | Yes